[quote author=Mike Sokol link=topic=150364.msg1378869#msg1378869 date=1404081190]Of course generators in parallel mode are at 0 degree phase angle (so no triplen harmonics), and even if they were running at 180 degrees for a true 240/120 volt output, there's still no triplen currents. [/quote]

Triplen harmonic currents do in fact exist in the neutrals of single-phase systems. In paralleling applications, the most troublesome of the triplen harmonics, the 3rd, can even exist when there is no load. 

Since some of these terms might be foreign to your readers, let’s start with some basics: there is available on the web a very informative article by Gary Olson, Technical Support for Cummins Power, on “Paralleling Dissimilar Generators.” To summarize that article: the voltage waveform shape created by a generator is not an ideal sinusoid and no two machines are the same. Furthermore, its' shape is also effected by its' load. The resulting waveform may be described in terms of its fundamental frequency and voltage magnitude and the magnitude of the harmonic voltages and their frequencies that make it up. This harmonic voltage distortion, while small in the case of inverter generators, may still be significant, particularly in paralleling applications. 

[center][img]http://www.screenlightandgrip.com/images/generators/Pro_Sound_Paralleling_Copy_Harmonic_Content.jpg[/img] 
(Harmonic Content of a Generator's Voltage Waveform)[/center]

The illustration above shows the relationship of first-order (fundamental frequency waveform) to third- and fifth-order harmonic waveforms of the resulting waveform. The harmonic voltages are effectively added to the fundamental waveform, resulting in the pure sinusoidal shape of the fundamental being somewhat distorted. For example, the resultant voltage at time A in the figure above will be the sum of the blue (fifth-order), green (third-order), and red voltage magnitudes. So, the instantaneous voltage at that instant in time would be somewhat higher than the voltage of the fundamental. 

When generators are paralleled, the voltage of the two machines is forced to the exact same RMS voltage magnitude. Differences in the harmonic make up of the voltage waveforms result in current flowing in the common neutral conductor between the two machines even when there is no load. This is referred to as circulating neutral current (also called “cross current.”) Its’ source is illustrated below. 

[center][img]http://www.screenlightandgrip.com/images/generators/Pro_Sound_Paralleling_Copy_3rd_Harmonic_Generation.jpg[/img]
(How 3rd Harmonics are generated)[/center]

In this illustration, two voltage waveforms of the same RMS value (the red and blue lines) are superimposed upon each other. Note that even though these voltage waveforms have the exact same RMS magnitude (they would read the same on a true RMS meter), at different points in time the blue voltage is higher than the red, and vice versa. Since there exists potential (voltage) between the two machines at these points, when the machines are connected together on a common bus, current will flow between the machines (cross current) even if there is no load. Note that because the blue and red voltage lines cross each other three times in each half cycle, the cross current includes a 3rd harmonic component (this current is represented by the green line.) 

The process of mathematically deriving the frequency components of a distorted periodic waveform is achieved by a technique known as a Fourier Transform. Microprocessor based test equipment, like power quality meters, can do this mathematical analysis very quickly using a technique known as an FFT (Fast Fourier Transform) which it displays as a bar graph. Each bar represents the magnitude of a harmonic frequency, be it voltage or current. Below is a power quality meter reading of the neutral cross-current that circulates between two Honda EU6500s operating in parallel mode with no load. 

[img]http://www.screenlightandgrip.com/images/generators/Pro_Sound_Paralleling_Copy_Test_CC-No_Load.jpg[/img]

Even with no load on the generators (not even our transformer/distro) there is roughly two amps of neutral current with a significant 3rd harmonic component. So, there do exist zero sequence triplen currents (the 3rd harmonic) when generators are operating in parallel at 0 degree phase angle. And because the neutral systems of the two machines are tied together into a common neutral bus, this cross current will continuously circulate (as illustrated below) between the two generators. 

[center][img]http://www.screenlightandgrip.com/images/generators/Pro_Sound_Paralleling_Copy_Circulating_Cross_Current.jpg[/img]
(The illustration above is for a 3-Phase System - the same principles apply to Single-Phase Systems)[/center]

Though not significant without a load, this cross current can become a problem under certain circumstance if we add to it the triplen harmonics dumped into the neutral by non-linear loads such as non-power factor corrected HMIs, Kinos, & LED lights. Because these harmonic currents (the triplens and the 3rd harmonic of the cross current) are in phase with one another they do not cancel in the neutral as fundamentals do, but instead build one on the other to create elevated cross current with a large 3rd harmonic component that circulates continuously on the neutral conductors. And, because the elevated 3rd harmonic cross current is at a higher frequency (180Hz) it generates a lot of heat, resulting in the overheating of conductors and the generator's inverters (more on this latter.)

I believe what gets Mike’s “bullshit-o-meter” reading high is the commonly held assumption that zero sequence triplen harmonic currents can’t exist in single phase systems as they do in three phase systems – they do. Under balanced load conditions they are minimal, but in out of balance conditions they can be significant. Let’s start with where this assumption comes from. 

[center][img]http://www.screenlightandgrip.com/images/generators/Pro_Sound_PP_Image85_IA.jpg[/img]
[/center]
In a power quality workshop I developed for IATSE Local 481 (New England Studio Mechanics) I demonstrate the source of elevated neutral return currents using a non-linear load that is used by the hundreds on motion picture stages for CGI production: the Kino Flo Image 85.

[center][img]http://www.screenlightandgrip.com/images/generators/Pro_Sound_PP_Image85_Specs.jpg[/img][/center]

As you can see in the Power Point slide from the workshop above, Image 85s are rich in harmonics with a THD of 77% and a large triplen component (3rd, 9th, & 15th.) 

[center][img]http://www.screenlightandgrip.com/images/generators/Pro_Sound_PP_Image85_Set-Up.jpg[/img][/center]

In the workshop I demonstrate how and why these non-linear lighting fixtures can lead to elevated neutral returns in 3-phase systems by watching what happens on a power quality meter as fixtures on separate legs of the service are turned on one at a time (set-up pictured above)

[center][img]http://www.screenlightandgrip.com/images/generators/Pro_Sound_Neutral_3ph_Har_Image85_Comp_Sm.jpg[/img][/center]

As you can see in the power quality readings above, absent phases B & C, the Image 85 on phase A returned 9A to the neutral (left picture.) When the Image 85 on phase B is switched on, and it returns another 9A to the neutral conductor, the current on the neutral climbs to 12.71A (center picture.) And, finally, when the Image 85 on phase C is switched on, and it returns another 9A to the neutral conductor, the current on the neutral climbs to 15.86A (right picture.)  Even though the three phases are perfectly balanced (9A on each) the current on the neutral is 176% of any one of the individual phase legs. Clearly, there is some cancellation between the phase legs going on (otherwise the neutral would be carrying 27A), but it is not complete cancellation. Why? 

When we dump return current from each leg into the “stew pot” of the common neutral, out of phase current cancels. The Fundamentals (A1,B1,C1 ) cancel each other out. The positive sequence harmonics (4th,7th, etc.) cancel each other out. The negative sequence harmonics (2nd, 5th etc.) cancel each other out. But, the zero sequence harmonics (3rd, 9th, 15th, etc.) do not cancel each other out.  Instead they add. Why?

If, for a moment, we consider only the 3rd harmonic (180 Hz) of each phase as they return on the neutral, you will notice in the illustration below that in each positive half-cycle of any of the fundamental waveforms, there are exactly two positive half-cycles and one negative half-cycle of 3rd harmonic.  

[center][img]http://www.screenlightandgrip.com/images/generators/Pro_Sound_1phase_3ph_cancellation_Sm.jpg[/img][/center]

The net result, as illustrated above, is that the 3rd-harmonic waveforms of three 120 degree phase-shifted fundamental-frequency waveforms are actually in phase with each other and so stack on one another rather than cancel out as the fundamentals, positive, and negative sequence harmonics do. The phase shift figure of 120o generally assumed in three-phase AC systems applies only to the fundamental frequencies, not to their harmonic multiples. A closer look at the harmonic currents making up the neutral return of our demonstration setup reveals that, though made up primarily of the third harmonics from each phase stacking one on another, the high neutral current also consists of the, 9th, and 15th harmonics from each phase stacking one on another as well. 

Due to their significance in three-phase power systems, the 3rd harmonic and its zero sequence multiples have their own special name: triplen harmonics.  All triplen harmonics add with each other in the neutral conductor of a 4-wire wye-connected load. In power systems containing substantial nonlinear loading, the triplen harmonic currents may be of great enough magnitude to cause neutral conductors to overheat. If returned to a generator they are induced into the generator’s Stator & Rotor coils where they circulate until dissipated as heat.

[center][img]http://www.screenlightandgrip.com/images/generators/Pro_Sound_1ph_cancellation_Sm.jpg[/img][/center]

As is evident in the illustration above, it is an altogether different situation in single-phase systems. Since the phase angle between legs is 180 degrees rather than 120 degrees, 3rd harmonic currents are also out of phase and will for the most part cancel just as the Fundamentals do. This is evident in the power quality meter reading below of the neutral of a single-phase system for first just one Image 85 on one leg (left) and then a 2nd Image 85 on the other leg which is 180 degrees out of phase (right.) As you can see here, when the two legs of a single-phase system are perfectly balanced (9 Amps on each) the triplen currents generated by a non-linear load will nearly cancel out – but not completely.

[center][img]http://www.screenlightandgrip.com/images/generators/Pro_Sound_Neutral_1ph_Har_Image85_Comp_Sm.jpg[/img][/center]

It is worth noting that the total harmonic distortion (THD) of the single-phase neutral current (98.3%) is as high as the three-phase neutral current (100%) – it just consists of higher order harmonic currents (other than the 3rd) at lower amplitudes. As we will see in a moment, even at these low amplitudes, the higher order harmonic currents will contribute to inverters overheating in paralleling operation.

While not canceling completely in the neutral, the triplen currents generated by non-linear loads do nearly cancel out. For this reason the harmonic currents generated by Cailen’s rig (switching power supply amplifiers, switching power supply console, powered wedges, and LEDs) may or may not elevate the cross current to dangerous levels – it depends on how evenly he loads his system. How much is too much will be discussed in a moment, but one thing is certain, because motion picture lighting crews, more often than not, can’t evenly load their systems the harmonic content of cross current reaches hazardous levels.
[bookmark: _GoBack]
[quote author=Tim McCulloch link=topic=150364.msg1379019#msg1379019 date=1404169898] Things like this get built to meet a particular need, not to sell bullshit to the unsuspecting.[/quote] 

The segment of the motion picture production industry using Honda generators (regional commercial spots, historical documentaries, and indie films - the market for which our system is designed), quite often are using them to power just one big light while they plug all their small lights into the location house power. The reason for this is that, as long as there is a sun and moon in the sky there is a need for a large HMI on interior and exterior sets because small HMIs, Kino-Flos, & LED light panels that can be plugged into wall outlets don't come close to balancing direct sunlight in day light scenes or covering deep background in night scenes. The go to fixtures in these segments of the market are HMIs ranging from 1.2 to 4kw. In this country the majority of HMIs in this range are not power factor corrected (as they are in Europe) and so they generate significant harmonic currents. For example, the power quality meter readings below are the distorted voltage and current waveforms created by a 4k HMI with non-PFC ballast operating on an EU6500is and their corresponding Fourier Transforms (note that the harmonic currents encountering the impedance of the generator create harmonic voltages at the same frequency.)
 
[center][img]http://www.screenlightandgrip.com/images/generators/Pro_Sound_Paralleling_Copy_Non-PFC_4k_Comp.jpg[/img] 
(L-to-R: Test Set-Up, Distorted Voltage (top) and current (bottom) waveforms, Corresponding Fourier Transformations (Voltage left and Current right)[/center]

These low budget productions compound the problem presented by the harmonics generated by large non-PFC lights by operating them on a single leg of a “Splitter Box.” 

[center][img]http://www.screenlightandgrip.com/images/generators/Pro_Sound_Splitter_Box.jpg[/img]
The Splitter Box pictured above breaks out the 240V power of a generator into two circuits with film style “Bates” receptacles as well as Edison receptacles.[/center]

Since Honda manufactures the EU6500 super quiet generator primarily for RV/home standby power, and not the film lighting market, their power output panels are not compatible with the larger motion picture lights. For this reason lighting rental houses have had to find ways to work around the limited power distribution panel that Honda puts on these generators. They do so by wiring custom distribution panels called “Splitter Boxes” that access more 120V power from the 240V twist-lock receptacle on the generators. While this approach worked well enough when the lighting loads placed on generators consisted predominantly of incandescent lights (a linear load), Splitter Boxes are inherently unsuitable to carry non-linear loads consisting predominantly of non-power factor corrected HMIs. To understand why this is the case, we must first appreciate why 240V circuits are provided on the generators in the first place (it is not to power motion picture lights) and how they work.

240V outlets are on generators to power common residential or industrial single-phase 240V loads. The most common are air conditioners, dryers, ranges, heaters, large motors, and compressors. If you look at the breaker of a 240V circuit on a building service panel that serves these loads, you will notice that they use two pole breakers - either 30A or 50A. Each pole of the breaker is in a sense an independent 30A or 50A 120V circuit. That is, if you measure the voltage from each pole of the breaker to ground it will be 120 volts, and if you measure the voltage between the two poles of the breaker you will notice that it is 240 volts. As illustrated below, the 120 volts of the two poles add up to 240V because the 120V circuits are on opposing legs of a single-phase service and 180 degrees out of phase of each other. In residential settings, this is how higher voltages are supplied to household appliances like dryers, electric ranges, air conditioners, motors, etc. that require more power than can be reasonably supplied by a single 120V circuit. 

[center][img]http://www.screenlightandgrip.com/images/generators/Pro_Sound_Voltage_Adds_to_240-Volts.jpg[/img]
The voltage of opposing legs of a single-phase circuit add while the current carried on the legs subtract.[/center]

Many of these household 240V receptacles, in fact, use a three-wire system (Hot, Hot, Ground, but no Neutral) because they are designed to power single-phase linear loads (like heating elements) that draw a perfectly balanced load and return no current.  Other 240V circuits use a 4-wire system (Hot, Hot, Ground, Neutral.) They include a single Neutral wire to provide a safe return for small 120V accessories in stoves and dryers like oven lights, clocks, and timers that throw off the balance. There need be only one Neutral wire for the two Hot wires because under normal applications the current on the Neutral is the difference between the Hot legs because of the phase cancellation. Since oven lights, clocks, and timers don’t draw much power, there is minimal current to return on the Neutral under normal applications. For this reason, the Neutral wire is typically the same size (10 Awg in this case) as that of the hot legs (remember the heating element of the stove/dryer operates a perfectly balanced single phase load and hence there is no return for the wire to carry from it). To service these same residential and industrial 240V loads, the 240V receptacles of portable gas generators are wired in a similar fashion with just one Neutral of the same size as the two hot legs (see wiring schematic below). 

[center][img]http://www.screenlightandgrip.com/images/generators/Pro_Sound_gen_wiring_sch.jpg[/img]
Generator Wiring Schematic[/center]

A Splitter Box works around the limitations of the generator power output panel, and provides additional 120V circuits, by splitting out the two 120V circuits that make up the 240V outlet. Splitter Boxes worked well enough back when the load on the 240V circuit consisted of only incandescent lights. As long as you roughly balanced your load between the two legs of the generator, phase cancellation between the legs resulted in the Neutral return being the difference between the legs and without a harmonic component. Things get a bit more complicated with non-linear lighting loads, especially in paralleling applications. 

As discussed previously, harmonic currents (particularly the 3rd) are troublesome. When they are dumped into the return of even a balanced single-phase distribution system, they do not entirely cancel and in fact add to the 3rd harmonic component of the no-load cross current that circulates continuously between the generators. And, when the load includes a large non-PFC HMI fixture that throws the system out of balance, the 3rd harmonic component contributed by the load, on top of that inherent in the no-load cross current, can result in cross current with a severely elevated 3rd harmonic component circulating between the generators.

I can’t demonstrate what would happen if one ran paralleled generators in an out of balance condition by operating the non-pfc 4k HMI mentioned above on one side of a single phase Splitter Box because, not being a big believer in Splitter Boxes, we don’t have any in our rental inventory. But, I can give you an idea of what would happen by running comparably size linear and non-linear loads on one side of a smaller Splitter Box on one generator.

[center][img]http://www.screenlightandgrip.com/images/generators/Pro_Sound_Paralleling_Copy_Test_CC_WS_Hor_NoReveal.jpg[/img]
(Note the yellow Splitter Box on the left provides only two 20A circuits from the 30A/240V receptacle on the generator. By comparison our 60A Transformer/Distro provides the 3 – 20A circuits of the black gang box in the center and a 60A circuit from the same 30A/240V receptacle.)[/center]

Let’s compare the cross currents circulated by two common loads (a 2kw quartz Fresnel and a 1.2kw HMI Par) under two different situations: when power is supplied by a Splitter Box with a common neutral (the yellow distro box on the left in the picture above) and when it is supplied by one of our Transformer/Distros without a neutral (the 60A Transformer/Distro supplying a 60A gang box on the right side of the picture above.) 

[center][img]http://www.screenlightandgrip.com/images/generators/Pro_Sound_Paralleling_Copy_Test_CC-No_Load.jpg[/img]
 (The 3rd Harmonic Content of neutral cross current with no load.)[/center]

As you can see in the power quality meter reading above, there is approximately 2.08A of cross current circulating between the two machines on a continuous basis even without a load. Of that 2.08A nearly a quarter of it (.39A) consists of 3rd harmonic current. As you can see in the picture below, powering a 2kw Quartz Fresnel by means of a Splitter Box does not add to the 3rd harmonic content of the cross current because it is a linear load. 

[center][img]http://www.screenlightandgrip.com/images/generators/Pro_Sound_Paralleling_Copy_Test_CC-2K_thru_SB.jpg[/img]
 (The 3rd Harmonic Content of cross current is not increased by the addition of linear loads like our 2kw Quartz Fresnel)[/center]

But, as is evident in the power quality meter reading below, it is an altogether different situation when the paralleled generators are powering a non-power factor corrected 1.2kw HMI. Even though the 1.2kw HMI draws roughly the same current as the 2kw Fresnel, because it is a non-linear load rich in harmonics it adds an additional 4.11 Amps of 3rd harmonic current to the continuously circulating cross current. 

[center][img]http://www.screenlightandgrip.com/images/generators/Pro_Sound_Paralleling_Copy_Test_CC-1.2K_thru_SB.jpg[/img]
(Powering a non-PFC 1200W HMI by means of a splitter box increases the 3rd Harmonic current circulating between the two generators by a factor of 150X.)[/center]

This 3rd harmonic content generated by the 1.2kw HMI is problematic because it will not cancel with the 3rd harmonic of the cross current generated by paralleling the generators. Where before, with a linear load, the 3rd harmonic made up 4% of the current circulating on the combined neutral, with the contribution of the 1.2kw HMI, the 3rd harmonic makes up nearly 60% of the current. And, because a greater percentage of this elevated cross current is at a higher frequency, it generates more heat (more on that latter.) 

[img]http://www.screenlightandgrip.com/images/generators/ProSound_Paralleling_4k_3&9th_Har_Comp_Sm.jpg[/img]

If this is the result of powering just one non-PFC 1.2kw HMI, powering a 4kw HMI on one side of a Splitter Box, without an equally large non-linear load on the other side to cancel it, will create severely elevated 3rd Harmonic current circulating between the two generators. As can be seen in the power quality readings above, in a situation where a non-PFC 4k HMI is operating on one side of a splitter box, significant 3rd, 5th,7th , and  9th harmonic currents will be contributed to the neutral by the 4kw HMI with no harmonic current contribution by the incandescent lights to cancel it out. The net result will be nearly 30 amps of primarily harmonic currents circulating continuously on the neutral with 94% of that consisting of Triplen harmonics (3rd= 26.2A, 9th= 2.1A.)

[quote author=Cailen Waddell link=topic=150364.msg1378865#msg1378865 date=1404078138]
The theory makes sense to me but they don't discuss the ampacity of the loads created by their indicated conditions, and I question whether it is enough to matter....[/quote]

While the 10 AWG neutral conductor of this system could handle (but just barely) a 30A cross current at 60Hz, it is an altogether different situation when the current includes higher frequencies. Similar to the “Eddy Currents” that will circulate in the secondary of a Delta/Wye transformer, cross current that consists primarily of harmonic currents will cause overheating of the Neutral (copper losses) and the generator’s inverters. The relationship of this “Eddy Current” heat loss to harmonic frequency is as follows:

[center][img]http://www.screenlightandgrip.com/images/generators/Pro_Sound_Paralleling_Copy_Overheating.jpg 
[/img]
(Where: PEC = Total eddy current losses, PEC-1 = Eddy current losses at full load based on linear loading only.
Ih = rms current (per unit) at harmonic h , and h = harmonic # ) [/center]


What is significant about the relationship of Eddy Current heat loss as a result of harmonic currents expressed in this equation is that the harmonic current (Ih) and harmonic number (h) are squared which means that instead of increasing in a linear fashion they increase exponentially. Put another way, the heat generated by harmonic currents just doesn’t increase gradually at higher harmonic frequencies, but it jumps drastically. In this discussion, we are focusing on the 3rd harmonic because, between the inherent no-load 3rd harmonic component of cross current and the contribution by non-linear loads, it can reach elevated levels. But, it is also worth noting that, as indicated in the equation above, higher order harmonics will generate as much heat as the 3rd, but at much lower amplitudes. For instance, according to the equation above 1 amp of the 5th harmonic will generate as much heat as 1.7 amps of the third. For this reason, the higher order harmonics (5th, 7th, 9th) of the generator cross current will also contribute to inverters overheating.

[center][img]http://www.screenlightandgrip.com/images/generators/Pro_Sound_Paralleling_Copy_Circulating_Cross_Current.jpg[/img]
(With a common neutral bus, cross current circulates continuously between generators operating in parallel)[/center]

It is also worth emphasizing that generators are particularly prone to overheating when used in parallel operation. That is because when generators are paralleled their neutrals are tied together into a common neutral bus and so the harmonically rich cross current generated by a non-PFC 4k HMI (consisting of not only the 3rd harmonic, but also the 5th,7th, & 9th) will circulate continuously between the two generators (as illustrated above), causing heat to build up to a catastrophic level. 
 
[center][img]http://www.screenlightandgrip.com/images/generators/Pro_Sound_EU7000_Honda_Paralleling_Prototype_Set-Up_Comp_Sm.jpg[/img]
(As the illustration of the prototype of Honda’s paralleling kit for the new EU7000 indicates, the generators are meant to provide only 240V power in paralleling operation.)[/center]

How much is too much harmonic content in cross current for inverter generators in parallel operation?  Honda is very tight lipped about their research, but we can infer from their design of the new paralleling capable EU7000is that even at low levels, harmonically rich cross current will cause inverters to burn out over time. For this reason, in the design of their new paralleling EU7000is, Honda incorporates noise filters where there are none in the EU6500is which was not designed for paralleling operation (see wiring schematic comparison below for details.)

[center][img]http://www.screenlightandgrip.com/images/generators/Pro_Sound_Inverter_Wiring_Schematic_EU7000-6500_Com_Sm.jpg[/img]
(A comparison of the red shaded areas of the wiring schematics of a EU6500is (top) verses that of a EU7000is (bottom) indicates that Honda engineers deemed it necessary to incorporate noise filters in the EU7000 even though it is meant to provide only 240V power in paralleling operation.)[/center]

It is worth noting that Honda’s paralleling system for their new EU7000is supplies only 240V power (Honda’s prototype paralleling box, illustrated above, includes only a 50A/240V Twist-lock receptacle.) That Honda’s engineers deemed it necessary to incorporate noise filters in generators that are designed to provide power to only 240V loads in parallel operations, loads that by their nature will not return harmonic currents on the neutral, is an indication of how damaging to inverters harmonically rich cross currents can be even at low amplitudes.

[img]http://www.screenlightandgrip.com/images/generators/Pro_Sound_Paralleling_Copy_No_Circulating_Cross_Current.jpg[/img]

One way to avoid the problems associated with even low-level harmonic currents continuously circulating on the Neutral, is to simply drop the Neutral. For this reason, we designed the electrical distribution of our paralleling set-up as a single-phase 240V system (Hot-Hot-Ground-no Neutral.) By removing the Neutral, we remove the path on which, not only the most disruptive current (the 3rd harmonic) can flow in a paralleling set up, but also higher order harmonic currents as well. On our system, HMIs 6kw and larger operate single-phase and hence return no harmonic currents to circulate as cross current. To operate 120V lights that require a Neutral (HMIs smaller than 6kw, Kinos, and Quartz lights), you would use either our 60 or 84 Amp Transformer/Distro to step-down the combined 240V of the generators to 120V as illustrated below.

[center][img]http://www.screenlightandgrip.com/images/generators/Pro_Sound_Paralelling_Copy_Trans_Gen_Isolation_Sm.jpg[/img]
(Our Transformer/Distros isolate triplen harmonics from the generators so that they can not elevate cross current to a hazardous level.) [/center]

The delta/wye configuration of our Transformer/Distros both create the required Neutral connection for smaller 120V loads, but at the same time isolate the generators from the 3rd harmonics created by these loads that would otherwise lead to elevated cross current, hot conductors, and overheated inverters. The harmonic currents generated by small HMIs, Kinos, & LEDs will cause heating of the primary of the Transformer/Distro (it can take it - it's a K-rated transformer), but the disruptive effect of their flow in the system Neutral of the paralleled generators is eliminated so the generator inverters remain cool. By eliminating a neutral connection between the gen-set bus and the loads, a Transformer/Distro eliminates the reason (overheating by harmonic currents) that prevented the successful parallel operation of EU6500s for 120V loads.

[center][img]http://www.screenlightandgrip.com/images/generators/Pro_Sound_Paralleling_Copy_Test_CC-1.2K_thru_Trans.jpg [/img]
(Powering the same non-PFC 1200W HMI by means of a Transformer/Distro instead virtually eliminates the 3rd Harmonic current circulating between the two generators.)[/center]

For example, when we remove the path on which the disruptive 3rd harmonic current generated by the 1.2kw HMI in our example above can flow back to our paralleling set-up by using our Transformer/Distro to power the light instead of the Splitter Box, the 3rd harmonic content of the cross current (as can be seen in the power quality meter reading below) is substantially reduced (by a factor of 150x) and so the generator’s inverters will operate a lot cooler and not melt down. By eliminating a neutral connection between the gen-set bus and the loads, a Transformer/Distro eliminates the reason (overheating by harmonic currents) that prevented the successful parallel operation of EU6500s for 120V loads - making it now possible to operate more lights, or larger lights, on portable Hondas than has ever been possible. 

Guy Holt, Gaffer 
ScreenLight & Grip 
Lighting Rental and Sales in Boston 
Cell 617-224-85634 
rentals@screenlightandgrip.com
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